## TCP
|  | SISTEMA INTEGRADO DE GESTION |  |  |  |  | CODIGO: DDA-FT-012
VERSION: 001
MAPA MODBUS CILA-2S
FECHA: 06-03-2021
PROTOCOLO: |  | MODBUS TCP |  |  |  |  | ODB:
VARIABLES DE LECTURA - TCP
Item | Nombre de Variable | Unidades | Minimo | Maximo | Dirrección MODBUS | TIPO | Tag MCM
0 | Actual Speed | HZ*10 | 0 | 32650 | 0 | Holding R. (INT)
1 | Actual Motor Voltage | Volt | 0 | 32650 | 1 | Holding R. (INT)
2 | Output Current | Amp*10 | 0 | 32650 | 2 | Holding R. (INT)
3 | Motor Current | Amp*10 | 0 | 32650 | 3 | Holding R. (INT)
4 | Selec_DHS 1 - SCHLUMBERGER 2 - CENTINEL 3 - ZENITH 4 - GRC SCOUT 5 - NONE 6 - NOVOMET 7 - BCPGRP SENSOR 8 - ZSP E7 | Selec_DHS * 10 | 0 | 9 | 4 | Holding R. (INT)
5 | Acel Ramp | Secs*10 | 0 | 32650 | 5 | Holding R. (INT)
6 | Decel Ramp | Secs*10 | 0 | 32650 | 6 | Holding R. (INT)
7 | Status C2S 0 - ESP RUNNING 1 - ESP STOPPED 2 - VSD ALARM 3 - GENERAL FAULT 4 - COMM. FAULT PF755 5 - TURNED OFF | Status CILA*10 | 0 | 32650 | 7 | Holding R. (INT)
8 | VSD Power KW | KW*10 | 0 | 32650 | 8 | Holding R. (INT)
9 | Min Speed Limit | HZ*10 | 0 | 32650 | 9 | Holding R. (INT)
10 | Primary Voltage | Volt*10 | 0 | 32650 | 10 | Holding R. (INT)
11 | Max Speed Limit | HZ*10 | 0 | 32650 | 11 | Holding R. (INT)
12 | Reserved | unitless | 0 | 32650 | 12 | Holding R. (INT)
13 | Direction 0 - Reverse 1 - Forward | unitless | 0 | 1 | 13 | Holding R. (INT)
14 | Reference Speed | HZ*10 | 0 | 32650 | 14 | Holding R. (INT)
15 | Reserved | unitless | 0 | 32650 | 15 | Holding R. (INT)
16 | DC Bus Voltage | Volt*10 | 0 | 32650 | 16 | Holding R. (INT)
17 | Reserved | unitless | 0 | 32650 | 17 | Holding R. (INT)
18 | VSD Temperature | ºF*10 | 0 | 32650 | 18 | Holding R. (INT)
19 | Power Factor | *10 | 0 | 32650 | 19 | Holding R. (INT)
20 | Reserved | unitless | 0 | 32650 | 20 | Holding R. (INT)
21 | Reserved | unitless | 0 | 32650 | 21 | Holding R. (INT)
22 | Reserved | unitless | 0 | 32650 | 22 | Holding R. (INT)
23 | Reserved | unitless | 0 | 32650 | 23 | Holding R. (INT)
24 | Reserved | unitless | 0 | 32650 | 24 | Holding R. (INT)
25 | Reserved | unitless | 0 | 32650 | 25 | Holding R. (INT)
26 | Reserved | unitless | 0 | 32650 | 26 | Holding R. (INT)
27 | Average Current | Amp*10 | 0 | 32650 | 27 | Holding R. (INT)
28 | Input Frecuency | HZ*10 | 0 | 32650 | 28 | Holding R. (INT)
29 | Average Kw | KW*10 | 0 | 32650 | 29 | Holding R. (INT)
30 | Average KVA | KVA*10 | 0 | 32650 | 30 | Holding R. (INT)
31 | Average KVAr | KVAr*10 | 0 | 32650 | 31 | Holding R. (INT)
32 | Input Power Factor | *10 | 0 | 32650 | 32 | Holding R. (INT)
33 | L1-L2 Voltage | Volts*10 | 0 | 32650 | 33 | Holding R. (INT)
34 | L2-L3 Voltage | Volts*10 | 0 | 32650 | 34 | Holding R. (INT)
35 | L1-L3 Voltage | Volts*10 | 0 | 32650 | 35 | Holding R. (INT)
36 | L1-N Voltage | Volts*10 | 0 | 32650 | 36 | Holding R. (INT)
37 | L2-N Voltage | Volts*10 | 0 | 32650 | 37 | Holding R. (INT)
38 | L3-N Voltage | Volts*10 | 0 | 32650 | 38 | Holding R. (INT)
39 | L1 Current | Amp*10 | 0 | 32650 | 39 | Holding R. (INT)
40 | L2 Current | Amp*10 | 0 | 32650 | 40 | Holding R. (INT)
41 | L3 Current | Amp*10 | 0 | 32650 | 41 | Holding R. (INT)
42 | L1 Power | KW*10 | 0 | 32650 | 42 | Holding R. (INT)
43 | L2 Power | KW*10 | 0 | 32650 | 43 | Holding R. (INT)
44 | L3 Power | KW*10 | 0 | 32650 | 44 | Holding R. (INT)
45 | Current Harmonics | %*10 | 0 | 32650 | 45 | Holding R. (INT)
46 | Voltage Harmonics | %*10 | 0 | 32650 | 46 | Holding R. (INT)
47 | Intake Pressure | psi | 0 | 32650 | 47 | Holding R. (INT)
48 | Discharge Pressure | psi | 0 | 32650 | 48 | Holding R. (INT)
49 | Intake Temperature | ºF | 0 | 32650 | 49 | Holding R. (INT)
50 | Discharge Temperature | psi | 0 | 32650 | 50 | Holding R. (INT)
51 | Motor Temperature | ºF | 0 | 32650 | 51 | Holding R. (INT)
52 | Casing Pressure | psi | 0 | 32650 | 52 | Holding R. (INT)
53 | Tubing Head Pressure | psi | 0 | 32650 | 53 | Holding R. (INT)
54 | Tubing Head Temperature | ºF | 0 | 32650 | 54 | Holding R. (INT)
55 | Voltage protection status | unitless | 0 | 32650 | 68 | Holding R. (INT) | 0:Normal, 1:Alarm L, 2:Alarm H, 3:LL Trip, 4:HH Trip
56 | Load protection status | unitless | 0 | 32650 | 69 | Holding R. (INT) | 0:Normal, 1:Alarm L, 2:Alarm H, 3:LL Trip, 4:HH Trip
57 | Vibration protection status | unitless | 0 | 32650 | 70 | Holding R. (INT) | 0:Normal, 1:Alarm L, 2:Alarm H, 3:LL Trip, 4:HH Trip
58 | Intake pressure protection status | unitless | 0 | 32650 | 71 | Holding R. (INT) | 0:Normal, 1:Alarm L, 2:Alarm H, 3:LL Trip, 4:HH Trip
59 | Intake temperature protection status | unitless | 0 | 32650 | 72 | Holding R. (INT) | 0:Normal, 1:Alarm L, 2:Alarm H, 3:LL Trip, 4:HH Trip
60 | Discharge pressure protection status | unitless | 0 | 32650 | 73 | Holding R. (INT) | 0:Normal, 1:Alarm L, 2:Alarm H, 3:LL Trip, 4:HH Trip
61 | Discharge temperature protection status | unitless | 0 | 32650 | 74 | Holding R. (INT) | 0:Normal, 1:Alarm L, 2:Alarm H, 3:LL Trip, 4:HH Trip
62 | Motor temperature protection status | unitless | 0 | 32650 | 75 | Holding R. (INT) | 0:Normal, 1:Alarm L, 2:Alarm H, 3:LL Trip, 4:HH Trip
63 | Tubing head pressure protection status | unitless | 0 | 32650 | 76 | Holding R. (INT) | 0:Normal, 1:Alarm L, 2:Alarm H, 3:LL Trip, 4:HH Trip
64 | Casing protection status | unitless | 0 | 32650 | 77 | Holding R. (INT) | 0:Normal, 1:Alarm L, 2:Alarm H, 3:LL Trip, 4:HH Trip
VARIABLES DE ESCRITURA - TCP
0 | Start | unitless | 0 | 1 | 55.0 | Holding R. (INT) | 0: No Action, 1:Start
1 | Stop | unitless | 0 | 1 | 55.1 | Holding R. (INT) | 0: No Action, 1:Stop
2 | Reset | unitless | 0 | 1 | 55.2 | Holding R. (INT) | 0: No Action, 1:Clear
3 | Reserved | unitless | 0 | 1 | 55.3 | Holding R. (INT)
4 | Reserved | unitless | 0 | 1 | 55.4 | Holding R. (INT)
4 | Speed reference | Hz*10 | 0 | 32650 | 56 | Holding R. (INT)
6 | Command direction | unitless | 0 | 32650 | 57 | Holding R. (INT) | 0: Forward, 1:Reverse
7 | Load HH setpoint | A | 0 | 32650 | 58 | Holding R. (INT)
8 | Load LL setpoint | A | 0 | 32650 | 59 | Holding R. (INT)
9 | Prolonged referencie | s | 0 | 32650 | 60 | Holding R. (INT)
10 | Intake pressure HH setpoint | psi | 0 | 32650 | 61 | Holding R. (INT)
11 | Intake pressure LL setpoint | pis | 0 | 32650 | 62 | Holding R. (INT)
12 | Intake temperature HH setpoint | ºF | 0 | 32650 | 63 | Holding R. (INT)
13 | Discharge temperature HH setpoint | ºF | 0 | 32650 | 64 | Holding R. (INT)
14 | Motor temperature HH Setpoint | ºF | 0 | 32650 | 65 | Holding R. (INT)
15 | Accel ramp setpoint | s | 0 | 32650 | 66 | Holding R. (INT)
16 | Deccel ramp setpoint | s | 0 | 32650 | 67 | Holding R. (INT)

## RTU
|  | SISTEMA INTEGRADO DE GESTION |  |  |  |  | CODIGO: DDA-FT-012
VERSION: 001
MAPA MODBUS CILA-2S
FECHA: 06-03-2021
PROTOCOLO: |  | MODBUS RTU |  |  |  |  | ODB: 2566293
VARIABLES DE LECTURA - RTU
Item | Nombre de Variable | Unidades | Minimo | Maximo | Dirrección MODBUS | TIPO | Tag MCM
0 | Actual Speed | HZ*10 | 0 | 32650 | 28692 | Holding R. (INT)
1 | Actual Motor Voltage | Volt | 0 | 32650 | 28693 | Holding R. (INT)
2 | Output Current | Amp*10 | 0 | 32650 | 28694 | Holding R. (INT)
3 | Motor Current | Amp*10 | 0 | 32650 | 28695 | Holding R. (INT)
4 | Selec_DHS 1 - SCHLUMBERGER 2 - CENTINEL 3 - ZENITH 4 - GRC SCOUT 5 - NONE 6 - NOVOMET 7 - BCPGRP SENSOR 8 - ZSP E7 | Selec_DHS * 10 | 0 | 9 | 28696 | Holding R. (INT)
5 | Acel Ramp | Secs*10 | 0 | 32650 | 28697 | Holding R. (INT)
6 | Decel Ramp | Secs*10 | 0 | 32650 | 28698 | Holding R. (INT)
7 | Status C2S 0 - ESP RUNNING 1 - ESP STOPPED 2 - VSD ALARM 3 - GENERAL FAULT 4 - COMM. FAULT PF755 5 - TURNED OFF | Status CILA*10 | 0 | 32650 | 28699 | Holding R. (INT)
8 | VSD Power KW | KW*10 | 0 | 32650 | 28700 | Holding R. (INT)
9 | Min Speed Limit | HZ*10 | 0 | 32650 | 28701 | Holding R. (INT)
10 | Primary Voltage | Volt*10 | 0 | 32650 | 28702 | Holding R. (INT)
11 | Max Speed Limit | HZ*10 | 0 | 32650 | 28703 | Holding R. (INT)
12 | Reserved | unitless | 0 | 32650 | 28704 | Holding R. (INT)
13 | Direction 0 - Reverse 1 - Forward | unitless | 0 | 1 | 28705 | Holding R. (INT)
14 | Reference Speed | HZ*10 | 0 | 32650 | 28706 | Holding R. (INT)
15 | Reserved | unitless | 0 | 32650 | 28707 | Holding R. (INT)
16 | DC Bus Voltage | Volt*10 | 0 | 32650 | 28708 | Holding R. (INT)
17 | Reserved | unitless | 0 | 32650 | 28709 | Holding R. (INT)
18 | VSD Temperature | ºF*10 | 0 | 32650 | 28710 | Holding R. (INT)
19 | Power Factor | *10 | 0 | 32650 | 28711 | Holding R. (INT)
20 | Reserved | unitless | 0 | 32650 | 28712 | Holding R. (INT)
21 | Reserved | unitless | 0 | 32650 | 28713 | Holding R. (INT)
22 | Reserved | unitless | 0 | 32650 | 28714 | Holding R. (INT)
23 | Reserved | unitless | 0 | 32650 | 28715 | Holding R. (INT)
24 | Reserved | unitless | 0 | 32650 | 28716 | Holding R. (INT)
25 | Reserved | unitless | 0 | 32650 | 28717 | Holding R. (INT)
26 | Reserved | unitless | 0 | 32650 | 28718 | Holding R. (INT)
27 | Average Current | Amp*10 | 0 | 32650 | 28719 | Holding R. (INT)
28 | Input Frecuency | HZ*10 | 0 | 32650 | 28720 | Holding R. (INT)
29 | Average Kw | KW*10 | 0 | 32650 | 28721 | Holding R. (INT)
30 | Average KVA | KVA*10 | 0 | 32650 | 28722 | Holding R. (INT)
31 | Average KVAr | KVAr*10 | 0 | 32650 | 28723 | Holding R. (INT)
32 | Input Power Factor | *10 | 0 | 32650 | 28724 | Holding R. (INT)
33 | L1-L2 Voltage | Volts*10 | 0 | 32650 | 28725 | Holding R. (INT)
34 | L2-L3 Voltage | Volts*10 | 0 | 32650 | 28726 | Holding R. (INT)
35 | L1-L3 Voltage | Volts*10 | 0 | 32650 | 28727 | Holding R. (INT)
36 | L1-N Voltage | Volts*10 | 0 | 32650 | 28728 | Holding R. (INT)
37 | L2-N Voltage | Volts*10 | 0 | 32650 | 28729 | Holding R. (INT)
38 | L3-N Voltage | Volts*10 | 0 | 32650 | 28730 | Holding R. (INT)
39 | L1 Current | Amp*10 | 0 | 32650 | 28731 | Holding R. (INT)
40 | L2 Current | Amp*10 | 0 | 32650 | 28732 | Holding R. (INT)
41 | L3 Current | Amp*10 | 0 | 32650 | 28733 | Holding R. (INT)
42 | L1 Power | KW*10 | 0 | 32650 | 28734 | Holding R. (INT)
43 | L2 Power | KW*10 | 0 | 32650 | 28735 | Holding R. (INT)
44 | L3 Power | KW*10 | 0 | 32650 | 28736 | Holding R. (INT)
45 | Current Harmonics | %*10 | 0 | 32650 | 28737 | Holding R. (INT)
46 | Voltage Harmonics | %*10 | 0 | 32650 | 28738 | Holding R. (INT)
47 | Intake Pressure | psi | 0 | 32650 | 28739 | Holding R. (INT)
48 | Discharge Pressure | psi | 0 | 32650 | 28740 | Holding R. (INT)
49 | Intake Temperature | ºF | 0 | 32650 | 28741 | Holding R. (INT)
50 | Discharge Temperature | psi | 0 | 32650 | 28742 | Holding R. (INT)
51 | Motor Temperature | ºF | 0 | 32650 | 28743 | Holding R. (INT)
52 | Casing Pressure | psi | 0 | 32650 | 28744 | Holding R. (INT)
53 | Tubing Head Pressure | psi | 0 | 32650 | 28745 | Holding R. (INT)
54 | Tubing Head Temperature | ºF | 0 | 32650 | 28746 | Holding R. (INT)
55 | Voltage protection status | unitless | 0 | 32650 | 28761 | Holding R. (INT) | 0:Normal, 1:Alarm L, 2:Alarm H, 3:LL Trip, 4:HH Trip
56 | Load protection status | unitless | 0 | 32650 | 28762 | Holding R. (INT) | 0:Normal, 1:Alarm L, 2:Alarm H, 3:LL Trip, 4:HH Trip
57 | Vibration protection status | unitless | 0 | 32650 | 28763 | Holding R. (INT) | 0:Normal, 1:Alarm L, 2:Alarm H, 3:LL Trip, 4:HH Trip
58 | Intake pressure protection status | unitless | 0 | 32650 | 28764 | Holding R. (INT) | 0:Normal, 1:Alarm L, 2:Alarm H, 3:LL Trip, 4:HH Trip
59 | Intake temperature protection status | unitless | 0 | 32650 | 28765 | Holding R. (INT) | 0:Normal, 1:Alarm L, 2:Alarm H, 3:LL Trip, 4:HH Trip
60 | Discharge pressure protection status | unitless | 0 | 32650 | 28766 | Holding R. (INT) | 0:Normal, 1:Alarm L, 2:Alarm H, 3:LL Trip, 4:HH Trip
61 | Discharge temperature protection status | unitless | 0 | 32650 | 28767 | Holding R. (INT) | 0:Normal, 1:Alarm L, 2:Alarm H, 3:LL Trip, 4:HH Trip
62 | Motor temperature protection status | unitless | 0 | 32650 | 28768 | Holding R. (INT) | 0:Normal, 1:Alarm L, 2:Alarm H, 3:LL Trip, 4:HH Trip
63 | Tubing head pressure protection status | unitless | 0 | 32650 | 28769 | Holding R. (INT) | 0:Normal, 1:Alarm L, 2:Alarm H, 3:LL Trip, 4:HH Trip
64 | Casing protection status | unitless | 0 | 32650 | 28770 | Holding R. (INT) | 0:Normal, 1:Alarm L, 2:Alarm H, 3:LL Trip, 4:HH Trip
VARIABLES DE ESCRITURA RTU
0 | Start | unitless | 0 | 1 | 28747.0 | Holding R. (INT) | 0: No Action, 1:Start
1 | Stop | unitless | 0 | 1 | 28747.1 | Holding R. (INT) | 0: No Action, 1:Stop
2 | Reset | unitless | 0 | 1 | 28747.2 | Holding R. (INT) | 0: No Action, 1:Clear
3 | Reserved | unitless | 0 | 1 | 28747.3 | Holding R. (INT)
4 | Reserved | unitless | 0 | 1 | 28747.4 | Holding R. (INT)
4 | Speed reference | Hz*10 | 0 | 32650 | 28748 | Holding R. (INT)
6 | Command direction | unitless | 0 | 32650 | 28750 | Holding R. (INT) | 0: Forward, 1:Reverse
7 | Load HH setpoint | A | 0 | 32650 | 28751 | Holding R. (INT)
8 | Load LL setpoint | A | 0 | 32650 | 28752 | Holding R. (INT)
9 | Prolonged referencie | s | 0 | 32650 | 28753 | Holding R. (INT)
10 | Intake pressure HH setpoint | psi | 0 | 32650 | 28754 | Holding R. (INT)
11 | Intake pressure LL setpoint | pis | 0 | 32650 | 28755 | Holding R. (INT)
12 | Intake temperature HH setpoint | ºF | 0 | 32650 | 28756 | Holding R. (INT)
13 | Discharge temperature HH setpoint | ºF | 0 | 32650 | 28757 | Holding R. (INT)
14 | Motor temperature HH Setpoint | ºF | 0 | 32650 | 28758 | Holding R. (INT)
15 | Accel ramp setpoint | s | 0 | 32650 | 28759 | Holding R. (INT)
16 | Deccel ramp setpoint | s | 0 | 32650 | 28760 | Holding R. (INT)